## Slide 1: Plastic Pipe Final Rule
2019 NV Safety Seminar

## Slide 2: Contact Information
Bryan Kichler
Transportation Specialist U.S. Department of Transportation PHMSA Inspector Training and Qualifications
Email: Bryan.Kichler@dot.gov

## Slide 3: Plastic Pipe Final Rule
DEPARTMENT OF TRANSPORTATION
Pipeline and Hazardous Materials Safety Administration
49 CFR Part 192
[Docket No. PHMSA-2014-0098: Amdt. No. 192-124] RIN 2137-AE93
Pipeline Safety: Plastic Pipe Rule

## Slide 4: SUMMARY
PHMSA is amending the Federal Pipeline Safety Regulations that govern the use of plastic piping systems in the transportation of natural and other gas. These amendments are necessary to enhance pipeline safety, adopt innovative technologies and best practices, and respond to petitions from stakeholders.

## Slide 5: SUMMARY
Higher pressures for PE and PA
Larger PA-11 pipe
Polyamide-12 pipe
More stringent standards for plastic fittings and joints
Updated testing requirements for joiners
New riser requirements
Category 1 mechanical fittings
Updated standards
New installation requirements
Equipment calibration requirements

## Slide 6: SUMMARY
DATES: The effective date of these amendments is January 22, 2019. The incorporation by reference of certain publications listed in the rule is approved by the Director of the Federal Register as of January 22, 2019.
AGA has petitioned for some changes to the rulemaking and extended implementation times

## Slide 7: New Definition
New
Weak link means a device or method used when pulling polyethylene pipe, typically through methods such as horizontal directional drilling, to ensure that damage will not occur to the pipeline by exceeding the maximum tensile stresses allowed.

## Slide 8: Standards Updates
Standard updates across the board for plastic pipe
Standard updates for fittings
Additional standards for PA-11 and PA-12 (polyamide)
Standard for repair of PVC segments

## Slide 9: Gathering lines
New
Newly constructed type B gathering lines must now comply with the plastic pipe requirements found in Part 192

## Slide 10: Inspection
192.59 now specifies that operators must verify that all pipe is free of visible defects prior to installation and permit the use of pipe that had been previously used in gas service other than natural gas.

## Slide 11: Updated Pipe Marking
192.63
Plastic pipe must now meet the marking requirements from the applicable specification for which it was manufactured

## Slide 12: Storage
New
192.67
Each operator must have and follow written procedures for the storage and handling of plastic pipe and associated components that meet the applicable listed specifications.

## Slide 13: Design
192.121 has been combined with 192.123
Design limitations have been merged into 192.121
Addition of PA-12 pipe
Larger diameters of PA-11
PA-11 and PA-12 tubing is now allowed
New installations of PA can operate up to 250 psig
New .40 design factor for PE (previously .32)

## Slide 14: Removed
192.123 has been removed and reserved

## Slide 15: Loading
192.143 General requirements.
For clarity, PHMSA added a new paragraph (c) to specify that components used for plastic pipe must be able to withstand operating pressures and anticipated loads in accordance with a listed specification, as defined in 192.3.

## Slide 16: Valves
192.145
PHMSA has added a new paragraph (f) to specify that plastic valves must be designed to meet a “listed specification” as defined in 192.3 and not operated in conditions that exceed the applicable pressure or temperature ratings detailed in the applicable listed specification.

## Slide 17: Fittings
192.149 Standard fittings.
(c) Plastic fittings installed after January 22, 2019, must meet a listed specification.
Section 192.191 Design Pressure of Plastic Fittings Removed and Reserved

## Slide 18: Risers
New
192.204 Risers installed after January 22, 2019.
  (a) Riser designs must be tested to ensure safe performance under anticipated external and internal loads acting on the assembly.
  (b) Factory assembled anodeless risers must be designed and tested in accordance with ASTM F1973–13

## Slide 19: Risers
New Cont.
192.204 Risers installed after January 22, 2019.
  (c) All risers used to connect regulator stations to plastic mains must be rigid and designed to provide adequate support and resist lateral movement.
  Anodeless risers used in accordance with this paragraph must have a rigid riser casing.

## Slide 20: Joining of PVC
192.281
Solvent cements are now to comply with ASTM D2564-12
The joint may not be heated or cooled to accelerate the setting of the cement.

## Slide 21: Joining of PE
192.281 Cont.
All heat fusion joints other than electrofusion must comply with ASTM F2620-12

## Slide 22: Socket Fusion
192.281 Cont.
A socket heat-fusion joint must be joined by a device that heats the mating surfaces of the pipe or component, uniformly and simultaneously, to establish the same temperature. The device used must be the same device specified in the operator's joining procedure for socket fusion.

## Slide 23: Electrofusion
192.281 Cont.
(c)(3) An electrofusion joint must be made using the equipment and techniques prescribed by the fitting manufacturer, or using equipment and techniques shown, by testing joints to the requirements of 192.283(a)(1)(iii), to be equivalent to or better than the requirements of the fitting manufacturer.

## Slide 24: Mechanical Fittings
192.281 Cont.
(e)(4) All mechanical joints or fittings installed after January 22, 2019, must be Category 1 as defined by a listed specification for the applicable material, providing a seal plus resistance to a force on the pipe joint equal to or greater than that which will cause no less than 25% elongation of pipe, or the pipe fails outside the joint area if tested in accordance with the applicable standard.

## Slide 25: Qualifying Joining Procedures
192.283 Plastic pipe: Qualifying joining procedures.
  (a) Heat fusion, solvent cement, and adhesive joints. Before any written procedure established under 192.273(b) is used for making plastic pipe joints by a heat fusion, solvent cement, or adhesive method, the procedure must be qualified by subjecting specimen joints that are made according to the procedure to the following tests, as applicable:

## Slide 26: Qualifying Joining Procedures
192.283 Cont.
Testing Thermoplastic Pipe
  Sustained Pressure Test or the Minimum Hydrostatic Burst Test
Testing Electrofusion Fittings
  Tensile Strength Test or the Joint Integrity Test
Testing Thermosetting Pipe
  Minimum Hydrostatic Burst Pressure or Sustained Static Pressure Test

## Slide 27: Qualifying Joining Procedures
192.283 Cont.
PHMSA is also repealing the obsolete 192.283(d), which allowed operators to install used pipe or fittings manufactured before July 1, 1980, if they are joined in accordance with procedures that the manufacturer certifies will produce a joint strong as the pipe.

## Slide 28: Plastic Joiner Qualification
192.285
Except for electrofusion, PE joints made during joiner qualification must be visually inspected and tested in accordance with ASTM F2620-12

## Slide 29: Bends
192.313
Section 192.313 details standards for bends and elbows in pipe, however, it did not previously address plastic pipe. This final rule adds a new paragraph (d) requiring that operators may only make bends in plastic pipe with a bend radius greater than the minimum bend radius specified by the manufacturer.

## Slide 30: Plastic Installations
192.321
Clarifications on protection of pipe on both entry and the exit of insertions
References to 192.123 have been moved to 192.121
Installations of risers at regulator stations must meet the design requirements of § 192.204.

## Slide 31: Trenchless Excavation
New
192.329 Installation of plastic pipelines by trenchless excavation.
Plastic pipelines installed by trenchless excavation must comply with the following:
  (a) Each operator must take practicable steps to provide sufficient clearance for installation and maintenance activities from other underground utilities and/or structures at the time of installation.
  (b) For each pipeline section, plastic pipe and components that are pulled through the ground must use a weak link, as defined by 192.3, to ensure the pipeline will not be damaged by any excessive forces during the pulling process.

## Slide 32: Pipe Connections
192.367
Similar to the new requirements for other fittings, paragraph (b) is amended to require that operators must use Category 1 compression-type fittings.
192.367 (b)(3) If used on pipelines comprised of plastic, be a Category 1 connection as defined by a listed specification for the applicable material, providing a seal plus resistance to a force on the pipe joint equal to or greater than that which will cause no less than 25% elongation of pipe, or the pipe fails outside the joint area if tested in accordance with the applicable standard.

## Slide 33: Trenchless Service Lines
New
192.376 Installation of plastic service lines by trenchless excavation.
Plastic service lines installed by trenchless excavation must comply with the following:
  (a) Each operator shall take practicable steps to provide sufficient clearance for installation and maintenance activities from other underground utilities and structures at the time of installation.
  (b) For each pipeline section, plastic pipe and components that are pulled through the ground must use a weak link, as defined by 192.3, to ensure the pipeline will not be damaged by any excessive forces during the pulling process.

## Slide 34: Corrosion
192.455
Electrically isolated metal alloy fittings installed after January 22, 2019, that do not meet the requirements of paragraph (f) must be cathodically protected, and must be maintained in accordance with the operator's integrity management plan.

## Slide 35: Testing
Section 192.513 details the minimum initial testing requirements for plastic pipelines. The final rule amends paragraph (c) to reduce the maximum limit for testing pressure from 3 times the pressure determined under 192.121 to 2.5 times the maximum pressure to avoid overstressing the line during testing.

## Slide 36: Repair Clamps
192.720 Distribution systems: Leak repair.
Mechanical leak repair clamps installed after January 22, 2019 may not be used as a permanent repair method for plastic pipe.

## Slide 37: Calibration and Maintenance of Equipment
New
192.756 Joining plastic pipe by heat fusion; equipment maintenance and calibration.
Each operator must maintain equipment used in joining plastic pipe in accordance with the manufacturer's recommended practices or with written procedures that have been proven by test and experience to produce acceptable joints.

## Slide 38: Questions? Thanks!
Bryan.Kichler@dot.gov